VILLAGE OF MAYBROOK

**WATER DEPARTMENT**

Village Hall @ 111 Schipps Lane

Maybrook, New York 12543

 **Telephone: (845) 427-2717, Fax: (845) 427-2164**

 **Board Meetings 2nd and 4th Mondays**

 **ANNUAL WATER SUPPLY STATEMENT FOR CALENDAR YEAR *2022*OF SYSTEM 3503533**

 The Village of Maybrook serves a population of approximately 3,300, within the Towns of Montgomery and Hamptonburgh. It services a portion of County Route 4 (AKA Maybrook Road). The **Water Supply** is obtained from 7 Bedrock Wells of an average depth of 357'. **The general quality** **of these sources is good, and** **is in compliance with New York State Department of Health and Federal** **EPA standards.**

***During 2022 the quantity of water from these sources exceeded the demand for consumption*,72,439,100** gallons **(198,463/day)** were treated and processed throughout the distribution system. A total **68,679,495**  gallons **(188,163/day)** was delivered to customers served by the Village of Maybrook. The difference of approximately **18,606**  gallons per day average is reflective of leaks both in the distribution system and residential, bi-annual hydrant flushing, watering of parks, street sweeping, firefighting operations, meter replacements and normal system losses. This difference represents a **8.99%** average for unaccounted water usage**. The national average for unaccounted for water loss is 35% 1 *water main break and 3 service line leak were discovered and repaired in 2022. 1large Water main leak on Homestead Ave, Service line leaks(these leaks were the responsibility of the property owner)and frozen/broken lines in unoccupied structures.*** The water department has the master meters calibrated annually. We periodically check for leaks with leak detection equipment, we also have a hydrant maintenance and replacement program and do residential leak detection on an as needed basis.

The water which is withdrawn from these sources, is treated with Chlorine for disinfection to destroy microorganisms. It is also treated with Polyphosphates for sequestering of Iron and Manganese (Naturally occurring Earth Elements) and corrosion control prior to delivery to our customers.

As always customers are advised to follow water conservation measures as posted on our website (***www.villageofmaybrook.com***) and if at all possible are asked to retrofit old plumbing fixtures with new water saving devices and to perform lawn and garden watering in an efficient manner. These measures can be expected to reduce future capital expenditures that may be necessary to increase the capacity of our water supply. **During 2021 ,** **the average water rate per residence was $4.15 per 1,000 gallons of** **water used, the commercial rate was $4.57 .**

**The Village has 2 State Certified Chief Water Treatment (Grade IIB) and Distribution System (Grade D) Operator, along with 2 State Certified Assistant (Grade C) Operators on staff. These operators are required to attend annual re-certification training in accordance with New York State DOH and EPA guidelines. We also keep in constant contact with the Orange County Department of Health and our Engineers regarding all aspects of our Water System.**

Due to the close proximity of the Nepera site to the wells (1,2,3) on County Route 4, the **Village is required to monitor** for **VOC's, POC’s, 625bn (Pyridine, Alphapyridine** and **Picoline)** at this site **quarterly**, in addition to all the other required annual testing. ***THERE WERE NO DETECTIONS OF ANY OF THESE CONTAMINANTS***

***The Village now is using the code red emergency warning system which allows us to notify you the consumer of any emergencies and work being done in the village. If you have not yet registered, please go to the village website (www.villageofmaybrook.com) for information on what the system can do for you. It includes notices that can be sent to cell phones, texting and voice mail along with landline information. This is also used for any type of public notifications.***

 **SWAP (source water assessment program) SUMMARY & EDUCATIONAL INFORMATION**

The New York State Department of Health completed a source water assessment for this system, based on available information. Possible and actual threats to this drinking water source were evaluated. The state source water assessment includes a susceptibility rating based on the risk posed by each potential source of contamination and how easily contaminants can move through the subsurface to the wells**. The susceptibility rating is an estimate of the potential for contamination of the source water, *it does not mean that the water delivered to consumers is, or will become contaminated.*** See “ Table of detected Contaminants” for a list of the contaminants that have been detected. The source water assessments provide resource managers with additional information for protecting source waters in the future.

As mentioned before, our water is derived from seven drilled bedrock wells. The source water assessment has rated these wells as having a medium to very-high susceptibility to microbials, nitrates, industrial solvents, and other contaminants. These ratings are due to primarily to the close proximity of a SPDES permitted discharge facility (industrial/commercial facilities that discharge wastewater into the environment and are regulated by the state and/ or federal government), the low-level residential activity and the waste site that are located in the assessment area. In addition, the wells draw from a confined aquifer with the estimated recharge area located within the selected time of travel and the overlying soils may not provide adequate protection from potential contamination. While the source water assessment rates our wells as being susceptible to microbials, please note that our water is disinfected to ensure that the finished water delivered into your home meets New York State’s drinking water standards for microbial contamination.

A copy of the assessment, including a map of the assessment area, can be obtained by contacting us, as noted in this report.

The Village has in effect, a set of **Watershed Rules and Regulations,** **which were adopted in 1982 by the New York State Health Department and are part** **of State Law. T**he **Village also** has a comprehensive **Wellhead Protection** plan to insure that our current and future wells are and will be protected from possible sources of contamination. The water department does 2 Annual inspections and submits a report to the Health Department. We also do periodic inspections of industrial facilities and the Nepera site to ensure the safety of our water sources.

**Drinking water, *including bottled water*, may reasonably be expected to contain at least small amounts of contaminants.** The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the EPA’s Safe Drinking Water Hotline (1 –800-426-4791).

**Because some people may be vulnerable to disease causing microorganisms or pathogens, New York State Law** requires water suppliers to notify their customers about the risks of cryptosporidiosis and giardiasis. Cryptosporidiosis and giardiasis are intestinal illnesses caused by microscopic parasites. **Cryptosporidiosis can be very serious for people with weak immune systems, such as those on chemotherapy, dialysis or organ transplant patients. People with Crohn's disease or HIV infection, also some elderly and infants can be at higher risks for infection.**  ***People with weakened immune systems should discuss with their health care providers the need to take extra precautions such as boiling water, using a certified bottled water or a specially approved home filter.*** Individuals who think that they may have either illness should contact their health care provider immediately**. The EPA/CDC has guidelines on appropriate means to lessen the risk of Cryptosporidium, Giardia and other microbial pathogens are available from the Safe Drinking Water Hotline @ (1-800- 426-4791).**

Since the Village’s Water sources are solely from deep bedrock wells (groundwater, 300’ to 500’), it is at very low risk for the presence of Giardia or Cryptosporidium, according to health experts in this field.

The sources of drinking water ***(both Tap Water and Bottled Water)*** include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As the water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and in some cases, radioactive material, and it can pick up substances resulting from the presence of animal or human activities. Contaminants that may be present in source water include, pesticides and herbicides, organic chemical contaminants and radioactive contaminants. In order to ensure that tap water is safe to drink, the State DOH and the EPA prescribe regulations, which limit the amount of certain contaminants in water provided by public water systems. The State Health Department’s and the FDA’s regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

For additional information on cryptosporidiosis or giardiasis, call the Orange County Health Department at (845) 291-2331. The New York State Department of Health can be contacted at (800) 458-1158 and the USEPA Drinking Water Hotline at (800) 426-4791.

 **ANNUAL WATER SUPPLY STATEMENT, CALENDAR YEAR 2022 DEFINITIONS:**

**The State Department of Health and the EPA require that definitions of terminology used in this report be supplied to the consumer. The following are the explanations of terms used for our testing results, possible sources of** contaminants that were detected and the associated health effects.

Entry Point: Is the point at which treated water enters the distribution system for the purpose of consumption. This is usually the first service connection, and in our case is at each of the well sites

**Maximum Contaminant Level Goal (MCLG):** The level of a contaminant in drinking water below, which there is no known or expected risk to health. MCLG’s allow for a margin of safety.

**Maximum contaminant Level (MCL)**: The highest level of a contaminant that is allowed in drinking water. MCL’s are set as close to the MCLG as possible.

**Action Level (AL)**: The concentration of a contaminant, which, if exceeded, triggers treatment, or other requirements, which a water system must follow.

**90th Percentile Value**: The values reported for **lead and copper** represent the 90th percentile value.

A percentile is a value on a scale of 100 that indicates the percent of the distribution that is equal to or below it.

The 90th percentile is equal to or greater than 90% of the lead and copper values detected in the sampling of the water system as set forth by the EPA guidelines.

**Unconfirmed Detection**: when a contaminant is detected in a water sample and subsequent repeat samples from the same location do not detect the same contaminant again.

Milligrams per Liter (mg/l) or Parts Per Million (ppm): corresponds to1 part of liquid in 1 MILLION parts of a liquid.

**Micrograms per Liter (ug/l) or Parts Per Billion (ppb):** corresponds to **1** part of liquid in **1 BILLION** parts of a liquid.

**Nanograms per Liter (ng/l) or Parts Per Trillion (ppt**): corresponds to **1 p**art of a liquid in **1 TRILLION** parts of a liquid

**Picocuries per Liter (pCi/l)** A measure of radioactivity in water

**Reduced Monitoring:** The frequency and number of samples required were reduced by the Department of Health because the initial sampling passed all applicable drinking water standards and subsequent samples again met drinking water standards.

**Non-Detectable: (ND)** Substance tested for was not detectable at the limits set forth by the EPA or DOH.

**Maximum Residual Disinfectant Level (MRDL)** The highest level of a disinfectant allowed in drinking water. There is convincing evidence that the addition of a disinfectant is necessary for control of microbial contaminants.

**Maximum Residual Disinfectant Level Goal (MRDLG)** The level of a drinking water disinfectant below, which there is no known or expected risk to health. MRDLG’s do not reflect the benefits of the use of disinfectants to control microbial contamination.

**TABLE OF DETECTED CONTAMINANTS:**

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| **Contaminant** **Detected** | **Violation** **Yes/No** | **Date of****Sample** | **Level Detected****(Avg./Max)****(Range)** | **Unit** **Measurement****Mg/l, ug/l** | **MCLG** | **Regulatory****Limit****(MCL, TT or Al)** | Likely Source of **Contaminant****Detected** |
| **Lead** | **NO** | **9/2021** | **3.2 \*(1)****ND – 3.5**  | **Ug/l** | **0** | **AL = 15** | **Corrosion of household plumbing** |
| **Copper** | **NO** | **9/2021** |  **0.99 \*(1)****0.07 – 1.5** | **Mg/l** | **1.3** | **AL = 1.3** | **Corrosion of household plumbing** |
| **Barium** | **NO** | **6/23/20** | **0.095** | **Mg/l** | **2** | **MCL = 2** | **Erosion of natural earth deposits** |
| **Iron** | **NO** | **5/14/19, 9/17/9****Well 2 raw samples.****6/20/19, 9/20/19, 10/6/19 distribution system samples** | **ND - 340** | **Ug/l** | **N/A** | **MCL = 300** | **Naturally occurring Earth Element** |
| **Nickel** | **NO** | **6/23/20** | **2.5** | **Ug/l** | **N/A** | **MCL = 100** | **Erosion of natural deposits** |
| **Manganese** | **NO** | **5/14/19,****9/17/19****Well 2 raw samples. 6/20/19, 9/20/19, 10/6/19 distribution system samples** | **ND - 1300** | **Ug/l** | **N/A** | **MCL = 300** | **Naturally occurring Earth Element** |
| **Sodium** | **NO** | **2022** | **34** | **Mg/L** | **N/A** | **See Health** **Effects** | **Naturally occurring, Road Salt**  |
| **Total Tri-Halomethanes** | **NO** | **8/2022** | **65** | **Ug/L** | **N/A** | **MCL = 80** | **By-product of drinking water chlorination to kill harmful organisms** |
| **Haloacetic Acids****(HAA5’s)** | **NO** | **8/2022** | **36.6** | **Ug/L** | **N/A** | **MCL = 60** | **By-product of drinking water chlorination needed to kill harmful**  |
| **Nitrate** | **NO** | **4/2021** | **ND – 0.78** | **Mg/l** | **10** | **MCL = 10** | **Erosion of Natural Deposits** |
| **Perfluorooctanoic Acid (PFOA) (2)** | **NO** | **2022** | **3.8** | **ng/l**  | **N/A** | **MCL = 10** | **Released into the environment from widespread use in commercial and industrial applications** |
| **Perfluorooctane sulfonic acid (PFOS) (2)** | **NO** | **2022** | **3.32** | **ng/l** | **N/A** | **MCL = 10** | **Released into the environment from widespread use in commercial and industrial applications** |

**\*(1)** The level presented represents the 90th percentile of the 10 sites tested. A percentile is a value on a scale of 100 that indicates the percent of a distribution that is equal to or below it. The 90th percentile is equal to or greater than 90% of the values detected at your water system. In this case, ten samples were collected at your water system and the 90th percentile value was the second highest value. The action level for lead was not exceeded at any of the sites tested; however, the action level for copper was exceeded at 1 of the sites tested.

(2) Please note that in addition to PFOS and PFOA, the lab ran the analysis for the entire EPA method 537.1, which includes 16 additional perfluorinated chemicals, **4** of these additional chemicals were detected, the highest of which was **4.22** ng/l. These additional analytes are not currently regulated and do not have an MCL.

 ***Please read the following educational information regarding lead in drinking water***

If present, elevated levels of lead can cause serious health problems, especially for pregnant women, infants, and young children. It is possible that lead levels at your home may be higher than at other homes in the community as a result of materials used in your home’s plumbing. The Village of Maybrook is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline (1-800-426-4791) or at http://www.epa.gov/safewater/lead.

 Infants and children who drink water containing lead in excess of the action level could experience delays in their physical or mental development. Children could show slight deficits in attention span and learning abilities. Adults who drink this water over many years could develop kidney problems or high blood pressure.

The copper and lead results are from our 2021 *reduced monitoring samples & additional sampling requirements.* Lead and Copper in household plumbing tends to build up when water is not used for long periods of time. The EPA suggests (flush before you brush) running the water until you get a noticeable temperature change before drinking.

Sodium: was detected from all sites ranging from 24(ppm) to 190 (ppm), There is no MCL: Sodium is naturally occurring and can come from road salt, *water softeners* and animal waste. Water containing more than 20 mg/l should not be used for drinking by people on severely restricted Sodium Diets. Water containing more than 270 mg/l should not be used for drinking by people on moderately restricted Sodium Diets.

A special note regarding Sodium in drinking water. Those homeowners with Water Softeners are reminded that water-softening devices use 46mg/l (ppm) of salt for every 100 mg/l (ppm) of water hardness (usually Calcium Carbonate CaCO3). Those on restricted sodium diets should consult their Physician.

Iron: was detected from the referenced site ranging from non-detectable to 340- 2000(ppb), MCL is 300(ppb): Iron is a naturally occurring earth element. The Samples from the distribution system (finished after sequestration treatment) were all Non Detectable, the detections referenced in the table were from raw(untreated) water samples.

*Iron has NO HEALTH EFFECTS*. At 1000(ppb) a substantial number of people will note the bitter astringent taste of iron. Also at 10(ppm) it imparts a brownish color to laundered clothing and stains plumbing fixtures with a characteristic rust color. Staining can result at levels as low as 50(ppb), lower than those detectable than the taste buds. Therefore the MCL of 300(ppb) represents a reasonable compromise as adverse aesthetic effects are minimized at this level. Many multivitamins contain 3000 (ppb) to 4000(ppb) per capsule (2 times the detected amount in our raw water).

Manganese: was detected from all sites ranging from non-detectable to 1300 - 1700 in (raw water) 15-33 (ppb) in the distribution system, MCL is 300(ppb): Manganese is naturally occurring and in excessive levels can be indicative of runoff from landfills. *The Food and Nutrition Board of the National Research Council determined an estimated safe and adequate daily dietary intake of manganese to be 2000(ppb) to 5000(ppb) for adults.* However, many people’s diets lead them to consume even higher amounts of manganese, especially those that consume high amounts of vegetables or who are vegetarians.

The sequestering procedure currently in use by the Village is used to maintain and stabilize the iron and manganese to reduce the sloughing process; also we flush our distribution system twice per year to achieve greater removal of deposits within the water mains.

The Village tests annually for Volatile Organic Chemicals (VOC’s, POC’c) of which there are a total of 55 possible contaminants (see attached list at end of report) additionally Nitrates are tested for annually.

The 2020 tests results for Synthetic Organic Chemicals (SOC’s, Pesticides), 45 total chemicals had no detections of these particular contaminants.

The Village also tests monthly for Bacteria (Coliform and E-Coli); there were no detections in 2022.

*A special note: Coliform bacteria, is naturally present in the environment. It can be found in the soil and on human skin. Coliform testing is used as an indicator mechanism to insure proper disinfection of the distribution system.*

*A complete supplement of the testing results is available for review at the DPW or Village Hall, or may be obtained by calling the office @ (845) 427–2717. If you have any questions concerning this report you may contact DPW Superintendent/Chief Operator Matthew A. Thorp @ (845) 427–2222 or the Orange County Department of Health @ (845) 291-2331, The State Department of Health @ (800) 458-1158 and the US EPA Hotline @ (800) 426-4791.*

Is Our Water System Meeting Other Rules That Govern Operation?

We are required to monitor your drinking water for specific contaminants on a regular basis. Results of regular monitoring are an indicator of whether or not your drinking water meets health standards. During 2022, we did not test for VOC's/POC's/Inorganics/Sodium/Nitrates from Wells 5,6,7 & 8 treatment facilites, and therefore cannot be sure of the quality of your drinking water during that time. This was due to the laboratory scheduling and pesonnel issues. It should be noted that we did test for these contaminants in April of 2023 and all results had no MCL exceedences and met drinking water standard.

CHEMICAL ANALYSIS REQUIRED

Group I and II Inorganics: Antimony, Arsenic, Barium, Beryllium, Cadmium, Chromium, Cyanides (total), Fluoride, Mercury, Nickel, Selenium, Sulfate and Thallium.

Volatile Organic Chemicals (VOC’s): Chloromethane, m.p-Xylene, Isopropylbenzene, Styrene, n-Propylbenzene, tert-Butylbenzene, sec-Butylbenzene, 1,3,5- Trimethylbenzene, 4- Isopropyltoluene, 1,2,4- Trimethylbenzene, Bromoethane, n-Butylbenzene, Hexachlorobutadiene, 1,2,4-Trichlorobenzene, Naphthalene,

1,2,3 Trichlorobenzene, MTBE, Dichlorodifluoromethane, Vinyl Chloride, Chloroethane, Methylene Chloride,

Trichlorofluoromethane, 1,1-Dichloroethene, Bromochloromethane, 1,1-Dichloroethane,

trans-1,2-Dichloroethene, cis-1,2- Dichloroethene, Chloroform, 1,2-Dichloroethane, 2,2-Dichloropropane, Dibromomethane, 1,1,1- Trichloroethane, Carbon Tetrachloride, Bromodichloromethane, 1,2- Dichloropropane,

1,1-Dichloropropene, Trichloroethene, 1,3- Dichloropropane, Dibromochloromethane, 1,1,2- Trichloroethane,

1,2- Dibromoethane, Bromoform, 1,1,1,2- Tetrachloroethane, 1,2,3- Trichloropropane,

1,1,2,2- Tetrachloroethane, Tetrachloroethene, Chlorobenzene, Bromobenzene, 2- Chlorotoluene,

 4- Chlorotoluene, 1,3- Dichlorobenzene, 1,2- Dichlorobenzene, 1,4- Dichlorobenzene, cis-1, 3- Dichloropropene, trans-1, 3-Dichloropropene, 1,2- Dibromo-3-Chloropropane, Benzene, Toluene, Ethylbenzene.

Synthetic Organic Chemicals (SOC’s): Aldicarb, Aldicarb Sulfone, Aldicarb Sulfoxide, Carbofuran, Oxamyl (vydate), Methomyl, 3-Hydroxycarbofuran, Carbaryl, Aroclor (1016, 1221, 1232, 1242, 1248, 1254, 1260), 1,2-Dibromoethane, 1,2-Dibromo-3-Chloropropane, Hepthachlor, Hexachlorocyclopentadiene, Atrazine, Heptachlor Epoxide, Dieldrin, Endrin, Methoxychlor, Alachlor, gamma-BHC (Lindane), Chlordane, Toxaphene, 2,4-D, 2,4,5-TP (Silvex), Pentachlorophenol (PCP), Dalapon, Dicamba, Dinoseb, Picloram,

 Di(2-ethylhexyl)adipate, Di(2-ethylhexyl)phthalate, Hexachlorobenzene, Benzene(a)pyrene, Simazine, Metachlor, Metribuzin, Butachlor, Hexachlorocyclopentadiene, Propachlor.

\*\*\* An additional note, information regarding all issues concerning our water and all Village Business can be found on our website [www.VillageofMaybrook.com](http://www.VillageofMaybrook.com). \*\*\*

FUTURE SYSTEM IMPROVEMENTS:

The village is currently looking for grant funding to replace the 86 year old water storage tank on Prospect Avenue as the repair/repainting costs are 75% of the cost to replace it. We have also started installing Variable Frequency Drives (VFD"s) to all the pumps at all treatment facilities to reduce energy costs and extend the life of all pumps and motors. We are also adding automated slow close valves at the treatment facilities to eliminate water hammer in the distribution system which will help to alleviate water main breaks. The Village has also started replacing the residential water meters for accuracy with cellular transmitters to allow readings to be done from the village office.

*The village also started the well rehabilitation of groundwater supply in 2017 using the Aquafreed process, along with the Aqua-gard system to allow us to do annual maintenance keeping the quantity and quality of our wells at optimum levels.* To date Wells 2, 3 , 7 (2017-2018), well 8 in 2019 have been done. *Eventually all wells will be rehabilitated and then maintained with Aqua-gard at least bi-annually*

If there are any questions please contact the DPW Superintendent/Chief Operator @ 845-427-2222 or mbkdpw@hvc.rr.com

Sincerely

Matthew A. Thorp

Chief Operator

Superintendent of Public Works